Market:

Power Generation

Challenge:

The challenge was to repair condenser water boxes that had become severely corroded. A solution was needed that would provide strength to the weakened structure and protect against future corrosion.

Engineered Solution:

The solution utilized the HydraWrap® Structural Composite Repair System.

Scope:

A customer requested repair and coating to four water boxes, each box measuring approximately 290 square feet. Engineers walked down the project, reviewed drawings, accessed system operating parameters, and provided an engineered solution.

Solution:

Each water box was grit blasted to SSPC-6 to obtain a near white surface profile. Two layers of bidirectional carbon fiber were installed on the interior surfaces of each water box while ensuring a smooth transition to all inlet and outlet connections. The HydraWrap® encapsulated all pinhole leaks and provided structural integrity to the wall area of the system.

HydraTech Engineered Products, LLC

HydraTech Field Services, LLC

10448 Chester Road, Cincinnati, Ohio 45215    Phone: (513) 827-9169    Fax: (513) 827-9171 http://www.hydratechllc.com

https://www.hydratechfs.com